## Slide 1: Best Practices for Plan Submissions
Erosion and Sediment Control (ESC) for minor projects
TAG THIS PRESENTATION @DOEE_DC
Notes: Thank you for joining the Best Practices for Plan Submissions training. We hope that this training will guide designers to include pertinent information in erosion and sediment control plan submissions so plan reviewers can efficiently review plans and reduce the amount of comments necessary. This training was developed because plan reviewers found that submittals had similar errors and misunderstandings. This training assumes some basic understand of ESC regulations and practices. I recommend watching or attending the other overview trainings prior to this one if you are not familiar with these.

## Slide 2
Objectives
@DOEE_DC
Know what information plan reviewers are checking
Know the most common comments and errors and how to avoid them
Review commonly misunderstood parts of the ESC manual/submission
Provide resources
Provide examples of good plan submissions
https://doee.dc.gov/swtraining
Notes: The objectives for this training are to learn what specific information plan reviewers are checking, learn the most common plan reviewer comments and the most common errors and how to avoid them, review commonly misunderstood parts of the ESC manual and the submission process, provide resources, and provide examples of good plan submissions. Overall, the goal of this training is to improve plan submittals to create a more efficient review process. Not everything in this training will be required, it may just be helpful for a plan reviewer to clearly understand the plans.
Additional training can be found at the website at the bottom of the slide

## Slide 3
Basic Plan Reviewer Methodology
@DOEE_DC
Review plans to understand project
  Drawings are clear and easy to understand
  All basic necessary components are shown and labeled on plans
  Plans are consistent with other disciplines, including LOD
Check that ESC measures meet design requirements
Notes: For a plan reviewer, they will typically first go through and review the plans to understand the overall project. The drawings should be clear and easy to understand and all required pieces should be included.

## Slide 4: Basic Plan components
@DOEE_DC
ESC

## Slide 5
Summary: Items to Include
@DOEE_DC
Vicinity plan
Area for approval stamp
Project description/narrative
Address, lot, square
Engineer/architect stamp and signature
North arrow
Scale
Lines, hatching and symbols in legend
Property boundaries
Street/alley labels
Clear, easy to read plans in a single PDF
Consistent information in Surface and Groundwater System (SGS)
Existing conditions
  Trees
  Grading
  Water areas

## Slide 6
@DOEE_DC
Lines are different weight and type to distinguish layer
Text is clear
Basic Plan Components – Example
Notes: Here is an example plan sheet that is very easy for a plan reviewer to read. Everything is clearly marked with differing line type of hatching and a legend.

## Slide 7
@DOEE_DC
Basic Plan Components – Example
Overlapping layers obscures information
Illegible references
Lines look too similar to distinguish
Notes: Here are examples of plans that are difficult to read and difficult for the plan reviewer to understand what is being represented. Overlapping layers that obscure the information below, such as spot elevations. Multiple lines with the same thickness and type make it very difficult to know what the lines are representing. Illegible references are also not allowed on plans.

## Slide 8
Basic Plan Components – Example
@DOEE_DC
Blank area- 7″ wide by 9.5″ tall and have a 1″ margin
Narrative
Vicinity map
Area for approval stamp
Address, lot and square
Signature and Stamp
Notes: 5907

## Slide 9
@DOEE_DC
Basic Plan Components – Example
North arrow and scale
Legend, include all line types, hatching and symbols
Include property lines
Street/alley label
Trees – show diameter at breast height (DBH) and critical root zone (CRZ: 1.5’ radius per inch DBH)
Notes: 6617

## Slide 10
Basic Plan Components – Example
North arrow
Street labels
@DOEE_DC
Symbols in legend match plans
Property lines
Signature and Stamp
Address, lot and square
Graphic scale
Notes: s16733

## Slide 11
Basic Plan Components – Example
Property lines
Street labels
Legends do not match plans
@DOEE_DC
Notes: s16504

## Slide 12
@DOEE_DC
Basic Plan Components – SGS

## Slide 13: ESC Measures
@DOEE_DC
ESC

## Slide 14
Summary: Items to Include
@DOEE_DC
Demolition plans
LOD
  PROW & utility work
Perimeter controls
Tree protection
Inlet protection
SCE
Stockpile
Sequence of construction
Area of disturbance
Cut/fill volumes
General description of the predominant soil type
DOEE General Notes
Dust Control Notes
Vegetative stabilization
ESC detail drawings

## Slide 15
LOD
ESC measures required before demo
ESC Measures – Example
Notes: 5907

## Slide 16
@DOEE_DC
ESC Measures – Example
Special and heritage trees- coordinate with DDOT UFD
Special and heritage trees- show critical root zone if in or near LOD (CRZ: 1.5’ radius per inch DBH in tree diameter)
Tree Protection
Notes: s16348

## Slide 17
ESC Measures – Example
Grading
LOD
Tree Protection
Inlet Protection
Stockpile
@DOEE_DC
Perimeter Controls
Notes: s15772

## Slide 18
@DOEE_DC
ESC Measures – Example
LOD and perimeter controls in legend but not on plan view
Notes: s15952

## Slide 19
ESC Measures – Example
SCE
DOEE general notes
perimeter controls fit site conditions
tree protection & CRZ
Stockpile with perimeter controls
@DOEE_DC
Disturbed area and cut/fill volume
Predominant soil type
(matches SGS)
LOD includes PROW & utility work
Notes: s16504

## Slide 20
@DOEE_DC
ESC Measures – Example
SCE
Notes: s16348

## Slide 21
ESC Measures – Example
@DOEE_DC
Area outside LOD likely to be disturbed
Notes: S16733 & s15952

## Slide 22
@DOEE_DC
ESC Measures – Example
Stockpile note
Note on LOD close to 5,000 sf
Notes: s15984

## Slide 23
@DOEE_DC
ESC Measures – Example
DOEE ESC General Notes
Dust control notes – Section 9.1
Area of Disturbance (square feet),
Volume of cut/fill (cubic yards)
Notes: s15952

## Slide 24
@DOEE_DC
ESC Measures – Example
Sequence of Construction
DOEE ESC General Notes
Disturbed area (square feet),
Volume of cut/fill (cubic yards)
Soil type
Notes: s15858

## Slide 25
USDA Soil Survey
@DOEE_DC
Click “START WSS”
Search by address

## Slide 26
USDA Soil Survey
@DOEE_DC
Define AOI by rectangle
Notes: Probably many ways to do this

## Slide 27
USDA Soil Survey
@DOEE_DC
General description of predominant soil type
Soil Reports tab
Map Unit
Description (Brief, Generated)
View Soil Report
Notes: Probably many ways to do this

## Slide 28
@DOEE_DC
ESC Measures – Example
Vegetative stabilization notes – Section 2.10
Completed Tables 2.3 (or 2.4) and 2.5
Notes: s15772

## Slide 29
@DOEE_DC
ESC Measures – Example
Relevant, legible details
2nd sheet
Notes: s15952

## Slide 30
Straw bale dike requires trenching
Cannot use on pavement or tree CRZ
@DOEE_DC
Paved Areas
Silt fence on pavement or filter sock
Tree CRZ
Tree root protection with silt fence or filter sock
ESC Measures – Perimeter Controls

## Slide 31: Comments and comment response letters
@DOEE_DC
ESC

## Slide 32
Each comment is addressed
Specify location of addressed comment (sheet)
Comment Responses – Good Example
Notes: Comment Response Letter
  Respond to each part of a comment if it's multi-part
  Specify on which sheets the comment was addressed
If there is any land disturbance in the PROW, follow procedure as outlined in Appendix B

## Slide 33
Does not indicate where information was added
Does not explain how comment was addressed or which sheet
Comment Responses – Bad Example

## Slide 34: Common Comments
@DOEE_DC
ESC

## Slide 35
Common Comments
@DOEE_DC
Upload the proposed plat to the SGS.
Enter all applicable DCRA building permit numbers associated with this project in the SGS.
Provide a blank area in the upper left-hand corner (must be 7 inches wide by 9.5 inches tall and have a 1-inch margin from top and left edge of page). This can be on a coversheet, if desired.
Enter the engineer/architect information in the SGS.
Provide the following documents:
  Environmental Intake Form – signed by DCRA
  Complete EISF report – if required by EIF
All plans must have a Sequence of Construction that describes implementation and maintenance of ESC measures and identifies permanent and interim stabilization practices. Include stages or phases of earth disturbance and construction.
Show the location of any stockpile areas and specify perimeter controls and stabilization methods.
Add a note indicating: The contractor must strictly limit disturbance to the approved LOD. If a DOEE inspector identifies disturbance outside the approved LOD, the project may be halted until stormwater management regulations are resolved.

## Slide 36
Common Comments
@DOEE_DC
Straw bale dike is not recommended as a primary sediment control device. Use tree protection with untrenched silt fence (DOEE Standard Detail 903.2) or untrenched filter sock (DOEE Standard Detail 303.1 and 303.2) within the critical root zone of trees to be preserved.
The architecture plans show that underpinning is to be done and new walls created in the basement. This is all considered land disturbance, and must be included in the LOD and cut/fill numbers.
Show a stabilized construction entrance (SCE).
Use silt fence on pavement (DOEE Standard Detail 310.1) or filter sock (DOEE Standard Detail 303.1 and 303.2) in paved areas.
Update the DOEE ESC General Notes with those found here: https://doee.dc.gov/esc.
Add Vegetative Stabilization notes to match the DC ESC Manual. Include completed Tables 2.3 (or Table 2.4) and 2.5.
Update the ESC details with the new specifications from the DC ESC Manual.
The ESC plan must include a general description of the predominant soil types on the site, as described by the appropriate soil survey information available from the USDA-NRCS.
Include the Dust Control construction specifications from Section 9.1 of the DC ESC Manual.

## Slide 37
Common Comments
@DOEE_DC
Show all existing trees on-site or close to the project. Including the trunk diameter at breast height (DBH) and the critical root zone (CRZ). The CRZ is defined as 1.5 ft of radius per 1 inch of DBH.
Show tree protection measures on the plan and provide details.
Streetview shows special and/or heritage trees along the back property lines. How will these be protected during construction?
Include a note on the plan to contact the Ward Arborist as soon as possible before construction begins to discuss tree protection measures. The Ward Arborist for this property is: xxxxxx, and their contact information is xxxx.xxxxx@dc.gov or 202-xxx-xxxx.
Enter all DDOT TOPS permit numbers in the Surface and Groundwater System (SGS), including tree removal permits.
Add inlet protection to the nearest down-grade stormwater catch basin.

## Slide 38: Resources available
@DOEE_DC
ESC

## Slide 39
Resources Available
@DOEE_DC
DOEE ESC webpage
  https://doee.dc.gov/esc
DOEE ESC Detail Drawings (CAD file), DOEE General Notes
  https://doee.dc.gov/node/619312
USDA-NRCS Web Soil Survey
  https://websoilsurvey.sc.egov.usda.gov/App/HomePage.htm
DDOT Urban Forestry – Tree Preservation
  https://ddot-urban-forestry-dcgis.hub.arcgis.com/pages/tree-preservation
PropertyQuest
  https://propertyquest.dc.gov/
Open Data DC – Arborist Zones
  https://opendata.dc.gov/datasets/arborist-zones?geometry=-77.063%2CNaN%2C-76.503%2CNaN